## Slide 1: Intelligent Infrastructure for Energy Efficiency Building Energy Use Les Norford
Residential (dorms):
Heating dominates
Control needed to avoid overheating
Commercial:
Lighting dominates
Less space heat due to internal gains

## Slide 2: Potential for wasted energy: simultaneous (same instant, same day) heating and cooling
Mild weather: perimeter may need heat in early morning, cooling in afternoon (like houses)
Year-round: core needs cooling constantly, even when perimeter must be heated
Perimeter zone
Core
173 kWh/m2 yr MA transp bldg (shown)
653 state office bldg
717 state office bldg
270 comm office bldg
196 comm office bldg
186 comm office bldg
The lower-energy buildings all recover heat from the building core
Open windows are another example

## Slide 3: Energy Waste Associated with Ventilation in a UK office
Sealed windows
100% mechanical conditioning
1+ year of monitoring and modeling
40 L/s-person
About four times code requirements
One-half expected occupancy
Conference rooms controlled design but CO2 levels were typically low
Heat-recovery system broken
EUI: 318 kWh/m2 as built
260 – est. with fixed heat recovery
228 - est. with heat recovery and lower ventilation

## Slide 4: Night cooling a California Courthouse
Results based on short-term tests and year-long simulation
15% whole-building electricity cost savings
Barrier: sensors and re-programming the HVAC control system

## Slide 5: High-speed measurement of electrical power for control and fault detection
Power profile of a commercial building
Onset of chiller evaporator vacuum leak

## Slide 6: Fluorescent lamps as proximity detector – lighting and airflow control
Notes: Because we are taking a differential measurement between two electrodes, a person passing under the lamp should result in a time-domain waveform that starts at the nulled voltage, deviates in one direction, then the other and finally returns to zero.
Above are plots of real data taken from a person walking under the lamp at 6 and 10 ft.
As 10 ft. is the current limit for our detection range, we can see random noise variations on that plot.