## Slide 1: I2E Data Sets
MIT Building N42: 100+ points of HVAC data from TAC
ASHRAE Building Energy Shootout data: 20 energy and HVAC data points
MIT Building NW35: 100+ points of HVAC data from Carrier and our sensors
Truro, Mass: 6,000 square foot high end home, 10+ points on HVAC equipment
MIT Enernet project with Senseable Cities – whole MIT campus, energy and HVAC (in coming months)

## Slide 2: I2E Initial Data Results
Air conditioning turns on 5 hours before occupancy
Early start HVAC also ignores the utility of cool outdoor air
10 MW-hrs
wasted this summer in early start HVAC.
Faulty early starts are 4% of annual energy
MIT Bldg. N42

## Slide 3: I2E Initial Data Results
AHU
GSHP
“Weekend” house fully operational on weekdays
Competing heating and cooling systems
Cycling of the unit
Data reveals natural system response.
Residence, Truro, Ma.

## Slide 4: I2E BT Activities
Data inference: statistical learning for appliance fault detection and opportunity identification
Interactive web portal for viewing energy data and marketing our project: i2e.mit.edu
“Geek Boxes” sensors, box, and support for deploying data system at MIT and beyond
Data acquisition infrastructure: software to gather data and perform systems integration

## Slide 5: I2E BT Going Forward
Near term (6 months):
  Stand-alone Matlab system for identifying and quantifying energy efficiency opportunities (inference and rules)
  Fully featured website for viewing building energy data
  Software for data collection
  “Geek Box” deployment at MIT, and integrate with MIT PI and TAC databases
Midterm (6-12 months):
  Pick up data sources outside of MIT:
    ANL
    San Cugat
    ???

## Slide 6: Intelligent Infrastructure for Energy Efficiency: Combining smarts with service
S. Samouhos
I2E Workshop
March 10th, 2009

## Slide 7: The Pain Within Buildings
Energy Costs
Operations Headaches
“Fire-fighting” action
Too many immediate problems
Too much data to review
Too few resources to plan ahead

## Slide 8: The Problem With Buildings
Information
Action
Data
We should fix them
We can fix them
But we don’t fix them?
Identify Opportunities
Quantify Opportunities
Sell Opportunities
Why?
WE NEED RESOURCES

## Slide 9: I2E Today: Data, Inference, Service
Opportunity
Identify
Quantify
Inform
Malfunction
Create Data
Present Opportunity
Review
Take Action
Fix Buildings
Data Acquisition
Data Inference
Service Execution

## Slide 10: I2E Inference will Answer:
“Is your machine/building running today like it did yesterday?”
“Which of your buildings should we target first for energy efficiency renovations?”
“Which appliance in your building should we fix first?”
“Does your building exhibit and any pathological energy in-efficiency behaviors?”
“Is your building/appliance worth fixing?”

## Slide 11: Data Inference Models
Expert Rules for e.g.
HVAC left on
HVAC competing
HVAC over-working
AI for
Performance changes
Relative comparisons
Building Energy Intelligence

## Slide 12
Classification Trees
Multivariate Process Control
RLS Classifier
Support Vector Machines – today’s weapon of choice
Neural Networks
AI Techniques for I2E – slide in progress

## Slide 13: SVMs
X1
X2
+1
-1
Optimization Problem
Training Error vs. Model Complexity
Accuracy vs. Generalization

## Slide 14: Test System: Truro, MA
2200 CFM Geothermal Heat Pump
Measure temperatures and air handler status
28 Days of data, measured at one minute intervals

## Slide 15: Test System Data
Transient heating
Constant EAT
Variable EWT
Reverse Cycling
Status Flutter

## Slide 16: Test System Data
System Lag
Thermal Lag
Non-unique Mapping

## Slide 17: Analysis Approach
Separate transient and steady state behavior
  Frequency space (machine cycle period)
  Run chart (Tair vs. water)
Create run-chart training data
  Identify “correct” operation: weighted balance of
    Observation frequency (relative counts)
    Observation sequence (sequential counts)
    Observation periodicity (absolute timing)

## Slide 18: Fault Detection: 28 Days
Twater (F)
8
0
4
30
15
Successfully classified correct operation
Screened False Positives
Successfully classified faulty operation
Heat Pump Performance Classifier
Total series classification
Successful fault detection
Polynomial kernel function
725 data points
8 Support Vectors
5 minutes computation time

## Slide 19: Applications
Integrate with Smart Grid to identify energy efficiency opportunities from AMI
Integrate with TAC and Carrier controls systems to scale into large commercial building stock
Web services to communicate efficiency opportunities to mechanical service contractors nationwide

## Slide 20: Immediate Next Steps
Classify on different time periods (days, weeks, etc)
Classify on frequency space (transient behavior analysis)
Matlab GUI for rapid model building/testing, and expert logic implementation
Explore other model techniques: RLS, Trees, MPC